## Slide 1: tuas wrp - a resource Recovery factory
Gokul Bharambe, Jacobs, Brisbane
Colin Newbery, Jacobs, Singapore
Peter Burrowes, Jacobs, Kitchener, ON, Canada
Mark Wong Wei Qiang, PUB, Singapore
Nunthinee Sundaramurthi, PUB, Singapore
Liow Wee Siang, PUB, Singapore

## Slide 2
Courtesy: Paul Reiter, IWA

## Slide 3
Courtesy: Paul Reiter, IWA

## Slide 4
Courtesy: Paul Reiter, IWA

## Slide 5: Disruptive Approaches are Needed to go from Treatment to Product Recovery
Nitrification
Basic Sanitation
TN & TP
Environmental Protection
cBOD & Solids
Nitrification
Increasing Level of Disruption
Wastewater Treatment
√
√
√
√
Used Water
Sustainability & Human Survival
Nutrient, Energy, Water
Chemicals
Metals
Biofuels
Biofplastics
?
Biorefinery
Bioplastic

## Slide 6
Maximise Energy Recovery
Minimise Land Take
Maximise Carbon Diversion
Maximise Water Reclamation
Minimise Energy
Consumption
Drivers
Drivers in Singapore

## Slide 7: Deep Tunnel Sewerage System (DTSS)

## Slide 8: TWRP Location and Footprint
Notes: Far West of Singapore
Reclaimed land

## Slide 9: Our Aims:
≈1km
≈1km
No compromise on Health & Safety
Maximise Water Reclamation
Minimise Energy Use
Optimise Land Use
Exploit synergies with IWMF to create a localised circular economy

## Slide 11: Site Layout
Influent Pumping Stations
Liquids (Domestic and Industrial Used Water) Treatment Facilities
Biosolids Treatment Facility
NW and IW Storage & Pumping
Wet Weather Treatment
Admin/O&M with Visitor Gallery
Future Expansions
F
F
F
F
Click number for more information

## Slide 12: Resources Recovered from Tuas WRP

## Slide 13: TWRP Key Features
Primary treatment design and flexibility
The advanced digestion process and THP design consideration
Digester geometry
Dewatered cake as fuel source
Highly efficient biogas use
Co-digestion

## Slide 14: Carbon Diversion
Flexibility provided in the process design to deliver an optimised C:N ratio in the bioreactor feed.
Integrated HRAS
50-70% COD diversion
Increase biogas production
Reduction in aeration demand
Conventional primary treatment
Integrated CEPT

## Slide 15: Advanced Digestion
WAS only THP selected
Higher net energy generation potential
Hydrolysed WAS allows for higher digester operating solids concentration
Increase in volatile solids destruction & digester biogas production
Increased dewaterability of digestate resulting in higher calorific value of sludge per wet tonne
Lower odor generation
Reduced quantity of solids requiring further handling
Allows increased volatile solids loading to the digester

## Slide 16: THP Design Consideration
Chart: tDS/d
| Average
PS- Domestic | 170
PS-Industrial | 46
WAS-Domestic | 55
WAS-Industrial | 44
Chart: tDS/d
| Average
Sludge to Hydrolysis | 99
Unhydrolysed sludge | 216

## Slide 17: THP Design Consideration
Chart: tDS/d
| Average
PS- Domestic | 170
PS-Industrial | 46
WAS-Domestic | 55
WAS-Industrial | 44
Chart: tDS/d
| Average
Sludge to Hydrolysis | 163.8
Unhydrolysed sludge | 151.2
Hydrolysis of sludge reduces Viscosity and allows digester to be operated at higher solids concentration.
50%

## Slide 18: Biosolids Treatment
Key Details:
  Multilevel biosolids building for thickening, pre-dewatering and dewatering centrifuges
  Thermal Hydrolysis pre-digestion to increase biogas production and energy recovery, as well as reduce sludge for disposal using steam from IWMF
  8 silo mesophilic anaerobic digesters co-digesting municipal biosolids with food waste and greasy waste
  Biogas transferred to IWMF to superheat the steam upstream of turbines to increase electricity production
  Sidestream nitrogen removal for the treatment of dewatering centrate
  Phosphorus sequestration
  Dewatered cake transferred to the IWMF for incineration and further energy recovery

## Slide 19: Digester Geometry
Silo Tall & Combined Egg / Silo
  Combines best features of both egg-shaped and tall
  Low mixing power required
  Virtually no grit buildup
  Easy scum removal
  Small footprint
  More expensive than conventional but less than egg

## Slide 21: What is Co-Digestion?
Simultaneous digestion of two or more substrates
Why co-digest?
Parameters | Food Waste | Sewage sludge (Conventional)
Micro-nutrients |  | 
Buffer capacity |  | 
Digestibility |  | 
Percent solids |  | 
Carbon : Nitrogen | Carbon source | Ammonia toxicity

## Slide 22: Co-Digestion at TWRP
Energy Feed Rate
COD/day
(PS + HWAS+ Food Waste + Greasy Waste)
Biogas
Energy Rate to IWMF
Specific Energy Loading Rate (SELR, kgCOD/day/kgVSS)
(Energy Feed Rate per mass of Volatile Solids in Digester)
Hydraulic Retention Time
Digester operating solids concentration
VS Loading Rate (kg VS/m3/d)
SELR
Dewatered Cake
to IWMF
Notes: Compare to Human Organic Loading Rate
300-770 kJ/day/kg solids based on
2000 kcal/day, 0.239 cal/J, 60% water, 150 lb or 68 kg total; 5000 kcal max

## Slide 23: TWRP-IWMF Synergies
*Note
Synergy 8: Ammonia Recovery from TWRP for IWMF’s use will be trialed after TWRP & IWMF have been commissioned
Material Handling Synergies
1) Food waste from IWMF to TWRP
2) Dewatered sludge from TWRP to IWMF
3) Screenings and grit from TWRP to IWMF
Energy Synergies
4) Power supply from IWMF to TWRP
7) Steam From IWMF to TWRP
5) Biogas from TWRP to IWMF
Water Synergies
6) Water From TWRP to IWMF
9) Condensate from IWMF to TWRP
Other Synergies
10) Chilled Water from IWMF to TWRP
8) Ammonia recovery from TWRP to IWMF
11) Admin Building and Carpark
TWRP: Tuas Water Reclamation Plant
IWMF: Integrated Waste Management Facility
9
10

## Slide 24
ILM
IWMF
IPS
DLM
NW/IW Storage and Pumping
Biosolids Treatment/Digestion

## Slide 25: tuas wrp - a resource recovEry factory
Gokul Bharambe, Jacobs, Brisbane
Colin Newbery, Jacobs, Singapore
Peter Burrowes, Jacobs, Kitchener, ON, Canada
Mark Wong Wei Qiang, PUB, Singapore
Charles Lim, PUB, Singapore
Nunthinee Sundaramurthi, PUB, Singapore
Liow Wee Siang, PUB, Singapore